## Slide 1: Global Trend in Industrial Refrigeration
Hernan Hidalgo
Global Account Manager – Danfoss Ind. Refrigeration
London Sep 30 2019

## Slide 2: Agenda
01.
Refrigeration Systems developments
02.
Trends in NH3 charge
03.
Typical Industrial Refrigeration system types
04.
Trends in Industrial Refrigeration Systems
08.
Oil return/recovery
09.
Conclusion
05.
Overview Transcritical cycle
06.
System Performance Comparison
07.
Systems Layout
08.
Defrost and Efficiency

## Slide 3: Why The Changes?
Industrial Refrigeration systems had enjoyed a higher degree of stability in terms of refrigerant choices.
Ammonia has been the predominant choice thanks to efficiency and heat transfer properties. Subcritical CO2 has been on the rise in Europe and North America
System Optimization has been key to development but also charge reduction in NH3 systems
In some developing economies, Urbanization is playing a significant role in the design and choice of refrigeration systems.
In some applications, Transcritical CO2 may be consider a good option.

## Slide 4
Super low
charge
NH3/CO2
NH3/DX
Refrigeration System Developments -Industry reaction
01.
Blending in of technologies and systems
Up to 150 kW
150 – 500 kW
500-1000 kW
1000-10000 kW
> 10000 kW
Capacity range
Definition of Industrial Refrigeration?
NH3?, CO2?, Steel?, Welding?, Capacity?, Pump circulation?
Charge reduction
Sub segment
Multi stage pumped
Single pumped
Typical NH3 systems
(steel/stainless,
welded connections)
Liquid ejector
gas ejector
Parallel compression
Booster
Single
HC
CFC, HFC,HFO systems
Technology
Commercial CO2 transcritical sytems

## Slide 5
4 MW ammonia system
Charge: 5 kg / kW
20.000 kg
Documented risk assessment.
Offsite risk assessment.
Safety quick closing section valves.
Safety gas detection.
Etc.
A
Increase general safety level of system.
R717-charge
1 x 20.000 kg
(5 kg / kW)
Design system with a number of sub-segments, which can be separated from each other in the event of leakage.
B
Sub-segments
R717-charge e.g.
4 x 5.000 kg
(5 kg / kW)
Install a number of rooftop mounted self-contained ammonia units
E
Low-charge Ammonia system
R717-charge e.g.
8 x 200 kg
(0,4 kg / kW)
CO2 booster system
CO2 TC
No R717-charge
F
Charge elimination
Ammonia DX-system reduce the required liquid charge
C
Ammonia-DX system
R717-charge e.g.
2 x 5.000 kg
(2,5 kg / kW)
Ammonia-CO2 cascade system or Ammonia-CO2 brine system
D
Ammonia-CO2
R717-charge
~2.000 kg
(0,5 kg / kW)
Charge reduction is an attractive mitigation solution
Trend to NH3 charge reduction
02.
How to reduce NH3 charge ?

## Slide 6
Industrial Systems
04.
Variables to consider
System Design
Capacities: 1 to 5 MW / 300TR to 1500 TR
Performance and Efficiency
Maximum pressure ratings
Components availability
Efficiency of evaporators/system due to fouling. (e.g. Oil)
Operators and contractors learning curve

## Slide 7: Refrigeration cycles with CO2 - General Overview
SUBCRITICAL
TRANSCRITICAL
TWO-STAGE
COMBINED

## Slide 8
35 oC [95 oF]
Transcritical refrigeration proces
Influence of compressor outlet pressure
80
[1160]
100
[1450]
90
[1305]
bar
[psi]
100 bar [1450 psi]
COP = 2,46
90 bar [1305 psi]
COP = 2,51
COP = (hEVAP*m )/ (hComp-is*m)
hComp-is
hEVAP
80 bar [1450 psi]
COP = 1,72
Max

## Slide 9
Trend to NH3 charge reduction
02.
Assessment of Emerging Systems Performance vs Traditonal
Fair Calculations have been made to provide an impartial assessment of industrial Ref Systems. (White paper presented at IRC Montreal 2019, Thomas Lund-Danfoss)
Two Stage R717, Pump circulation (2 Stage ) Baseline
R744/R717 cascade pump circulation
Transcritical R744 DX Operation
Transcritical R744 pump circulation
Two stage R507, Pump circulation

## Slide 10
Trend to NH3 charge reduction
02.
Calculations performed on three different latitudes 365 day

## Slide 11
Trend to NH3 charge reduction
02.
Compressor types used for calculations at different loads

## Slide 12
Trend to NH3 charge reduction
02.
Power Consumption comparison with NH3 as a baseline
Dry cooler with no correction for parallel compression

## Slide 13
Trend to NH3 charge reduction
02.
Power Consumption comparison with NH3 as a baseline
Bar graph TC flooded (recirculated) in warm climate does not include efficiency gain from parallel compression due to software constraints
 | CO2 TC DX | CO2 TC Flooded | R717 2ST | Cascade | R507 2ST
Rome | 129% | 121% | 100% | 105% | 106%
Frankfurt | 113% | 105% | 100% | 103% | 104%
Oslo | 108% | 100% | 100% | 103% | 103%
Table shows best possible results with adiabatic coolers and manual estimation with parallel compression for TC

## Slide 14
Typical Industrial Refrigeration system types
03.
The traditional NH3 pump circulation system
Fully dedicated IR built
Pumped systems on MT and LT
Dedicated compresssors per temperature level
Evaporative condensor
Industrial hotgas defrost
Oil return control
Complete system coordination
Steel/stainles steel pipes
Welded
Industrial built design
Reliabile and proven technology
+
Generally most efficient system
Superior cooler efficiency
Easy to control
Efficient and safe hotgas defrost
High safety integrity
Leak tight
Long litefime
New emerging technologies for charge reduction
-
NH3 charge
First costs
Condenser
NH3
LT compressor
MT compressor
100% 1)
NH3 pump circulation
with Danfoss Industrial valves and controls

## Slide 15
Fully dedicated IR built
CO2 pump systems on medium temp. and low temp.
Dedicated compresssors per temperature level
Evaporative condensor
Industrial hotgas defrost
Oil return control
System coordination
Steel/stainles steel pipes, welded
Industrial built quality
Reliable and proven technology
+
Up to 80% NH3 charge reduction
High efficienty compared to brine systems
Small CO2 compressor foot print
CO2 liquid overfeed
Superior cooler efficiency
Easy to control
Efficient and safe hotgas defrost
High safety integrity
Leak tight
Long litefime
-
Higher pressure
Cascade cooler
CO2 sub critical
NH3
CO2 pump circulation
03.
NH3/CO2 cascade system
Typical Industrial Refrigeration system types
Achieved with standard components rated at 754 psig

## Slide 16
Fully dedicated IR built
Pumped systems on MT and LT
Possibly DX on LY
Parallel compresssion
Air cooled gas coolers
Industrial hotgas defrost
Oil return control
System coordination
Gas ejector
Steel/stainles steel pipes, welded,
Industrial built
Stand still pressure 65 bar
+
No NH3
No superheat, so better efficiency
compared to CO2 TC DX
Better HTE
Better cooler efficiency
Easy to control
Efficient and safe hotgas defrost
High safety integrity
Leak tight
Long litefime
-
Less efficient compared to NH3
Racks:
Need many racks
Life time
Serviceability
Commercial compressors
Complex HP control system
LT
MT
IT
LT pumps
MT pumps
IT seperator
Ejector
CO2 sub critical
CO2 (transcritical)
Multiple racks parallel connected
CO2 pump circulation
The Industrial CO2 TC system
04.
Pump circulation and hotgas defrost
Ie 1-5 MW

## Slide 17
LT pumps
MT pumps
LT
MT
IT
IT seperator
HP valve
LT
MT
IT
IT seperator
HP valve
LT
MT
IT
IT seperator
HP valve
LT
MT
IT
IT seperator
HP valve
1) Industrial valves (2 temp. Levels, LT)
AK-PC 782A
AK-PC 782A
AK-PC 782A
AK-PC 782A
Transcritical
Subcritical
The industrial CO2 TC system
04.
The key elements
Connection
Rack controllers, MT and LT

## Slide 18
Static Height
Calculations dffer from those in NH3 systems
  Communication. Integration with central compressor package controllers and evaporators is key to balance the system
Industrial Pumped System
06.
Level Control of recirculators – Similar to NH3 systems

## Slide 19
Industrial Pumped System
06.
Hotgas defrost is by far the most efficient method compared to
Electric defrost: ~ ¼ of the efficiency
Glycol interlace: ½ of the efficiency

## Slide 20
Sub critical pressures
Transcritical pressures
LT
MT
IT
LT
MT
IT
LT
MT
IT
Trancritical racks typical PS = 120-140 bar
Industrial pump circulating system typical PS = 52 bar
Downstream pressure control
LT separator
MT separator
MT
evaporators
PC L
PC MT
The pressure in the sub critical system must be controlled
ALWAYS Focus on controlled and safe injection
Controlled defrost pressure between 7-12 degr.C
Take care of long lines and pressure loss (1 bar ~ 1 K)
Hotgas supply pressure to be controlled
Back up safety needed (internal pressure relief)
Final safety: external pressure blow off
Danfoss Industrial Pumped System
06.
2c) Hotgas supply for defrost

## Slide 21
Sub critical pressures
Transcritical pressures
Trancritical racks typical PS = 120-140 bar
Industrial pump circulating system typical PS = 52 bar
LT separator
MT separator
MT
evaporators
PC L
PC MT
Purpose
Send accumulated system oil back to the racks
LT
MT
IT
IT seperator
gas ejector
oil
CO2 TC rack 1,2,3,4,5
TC
oil
P
What to control?
Oil rectifier injection control
Oil collection receiver pressure
Oil circuit back to racks
Oil need signal frtom racks
Safety
Industrial Pumped System
06.
2d) Oil rectify – and oil return control
How ?
Oil rectifying system
Liquid injection
Receiver
pressure
Oil
return
Oil rectifier
System oil

## Slide 22: Conclusions
NH3 (ammonia) is still the most efficient refrigerant for Industrial Systems going forward
1
2
3
5
4
7
8
OEMs are investing in solutions to make these systems easier accessible
NH3/CO2, NH3 low charge or CO2 TC systems are possible options.
Transparent comparison of energy efficiency of different system types is extremely important!
09.
Commercial and Industrial CO2 TC systems are different-both due to different performance, lifetime, reliability and safety expectations!
The connection of the Industrial pump systems to a transcritical cycle world however demands some industry efforts
NH3 charge reduction (at same or better efficiency) remains an obvious goal and offer a significant lower regulatory burden
The viability of CO2 TC Systems in Industrial Refrigeration applications should become more clear in the next few years.
9
10
Larger transcritical CO2 compressor capacities are critical for further development of CO2 TC applications in Industrial Refrigeration
6
CO2 transcritical pump systems close the gap for mid size plant capacities when NH3 is not considered in the first place